| PWS Name: |  | PWS ID #: | 41 |
| --- | --- | --- | --- |
|  | Name | Telephone # |
| Operator in Direct Responsible Charge (DRC) |  | - - |
| Person that collected samples if different than DRC |  | - - |
| Date of Investigation: | MM/DD/YYYY |

INVESTIGATION DETAILS

| Groundwater Source Inspect each groundwater source for physical defects and report: | Well/Spring Name | Well/Spring Name | Well/Spring Name | Well/Spring Name | N/A | If Yes, describe issue |
| --- | --- | --- | --- | --- | --- | --- |
| 1. Cracks or holes in well seal or casing | Y N | Y N | Y N | Y N |  |  |
| 2. Wellhead lacks a watertight seal | Y N | Y N | Y N | Y N |  |  |
| 3. Screen for well vent missing or damaged | Y N | Y N | Y N | Y N |  |  |
| 4. Wellhead subjected to flooding or standing water near well | Y N | Y N | Y N | Y N |  |  |
| 5. Leaking sewer lines or septic tanks near well/spring | Y N | Y N | Y N | Y N |  |  |
| 6. Feces, fecal source observed near well/spring | Y N | Y N | Y N | Y N |  |  |
| 7. Unsanitary conditions at the well/spring | Y N | Y N | Y N | Y N |  |  |
| 8. Contamination during pump repair/replacement or other wellhead/spring repair | Y N | Y N | Y N | Y N |  |  |
| 9. Use of an unapproved or untested source | Y N | Y N | Y N | Y N |  |  |
| 10. Indication of surface water entering springbox | Y N | Y N | Y N | Y N |  |  |
| 11. Cracks or holes in springbox | Y N | Y N | Y N | Y N |  |  |

| Treatment and Disinfection Inspect each treatment plant for physical defects and report: | Plant Name | Plant Name | Plant Name | Plant Name | N/A | If Yes, describe issue |
| --- | --- | --- | --- | --- | --- | --- |
| 1. Inability to maintain residual throughout the distribution system | Y N | Y N | Y N | Y N |  |  |
| 2. Failure of disinfection equipment | Y N | Y N | Y N | Y N |  |  |
| 3. Failure to monitor and replace chlorine supply | Y N | Y N | Y N | Y N |  |  |
| 4. Improper chlorine residual measurements (method or frequency) | Y N | Y N | Y N | Y N |  |  |
| 5. Failure to meet required minimum chlorine residual at the entry point (GW only) | Y N | Y N | Y N | Y N |  |  |
| 6. Failure to meet CTs at all times (SW only) | Y N | Y N | Y N | Y N |  |  |
| 7. Failure to meet turbidity standards (SW only) | Y N | Y N | Y N | Y N |  |  |
| 8. Failure to meet filtration requirements (SW only) | Y N | Y N | Y N | Y N |  |  |

| Storage Tanks Inspect each storage tank for physical defects and report: | Tank Name | Tank Name | Tank Name | Tank Name | N/A | If Yes, describe issue |
| --- | --- | --- | --- | --- | --- | --- |
| 1. Holes in tank that could allow entry of insects or small animal | Y N | Y N | Y N | Y N |  |  |
| 2. Roof access hatch or other openings inadequately sealed | Y N | Y N | Y N | Y N |  |  |
| 3. Vent screens missing or damaged | Y N | Y N | Y N | Y N |  |  |
| 4. Screen or flap valve on overflow pipe outlet missing or damaged | Y N | Y N | Y N | Y N |  |  |
| 5. Presence of contamination in tank (example: dead animals, insects) | Y N | Y N | Y N | Y N |  |  |
| 6. Recent maintenance or work done on the tank | Y N | Y N | Y N | Y N |  |  |
| 7. Improperly cleaned or maintained storage tank | Y N | Y N | Y N | Y N |  |  |
| 8. Leaks in tank that could be harboring growth | Y N | Y N | Y N | Y N |  |  |
| 9. Inadequate tank controls resulting in poor turnover | Y N | Y N | Y N | Y N |  |  |
| 10. Bladder pressure tank waterlogged | Y N | Y N | Y N | Y N |  |  |

| Distribution System Inspect the distribution system for physical defects and report: | Yes/No | N/A | If Yes, describe issue |
| --- | --- | --- | --- |
| 1. Failure to maintain adequate pressure or low pressure event (example: pump failure leading to low pressure) | Y N |  |  |
| 2. Recent main break or repair of broken water lines | Y N |  |  |
| 3. New water lines or service connections added to the system | Y N |  |  |
| 4. Improper construction of new, replaced, or renovated lines or service connections | Y N |  |  |
| 5. Known leaks in the distribution system | Y N |  |  |
| 6. Supervisory control and data acquisition (SCADA) and control issues | Y N |  |  |

| Cross Connection and Backflow Inspect the system for cross connections and report: | Yes/No | N/A | If Yes, describe issue |
| --- | --- | --- | --- |
| 1. Unauthorized connections to water mains | Y N |  |  |
| 2. Known recent unprotected backflow incident | Y N |  |  |
| 3. Unprotected cross connection(s) discovered (ex. unprotected connection with a private well) | Y N |  |  |
| 4. Failure of installed backflow prevention devices (example: continuous discharge from the relief port on a device) | Y N |  |  |
| 5. Any water system components submerged in an underground vault | Y N |  |  |
| 6. Failure to test all backflow prevention devices within the last year | Y N |  |  |

| Sampling Protocol Report any defects in sampling protocol: | Yes/No | N/A | If Yes, describe issue |
| --- | --- | --- | --- |
| 1. Tap flushed for less than 3 minutes | Y N |  |  |
| 2. Aerator, screen, hose, or other attachment present during sampling | Y N |  |  |
| 3. Leaky or swivel faucet used | Y N |  |  |
| 4. Samples not kept cool during storage/transportation | Y N |  |  |
| 5. Inside of bottle/lid touched or lid set down | Y N |  |  |
| 6. Heavy rainfall or wind at time of sampling | Y N |  |  |
| 7. Sampled at site not on coliform sampling plan or previously unused site | Y N |  |  |
| 8. Other sampling problems | Y N |  |  |

| General Operations Report any defects in general operation of the system: | Yes/No | N/A | If Yes, describe issue |
| --- | --- | --- | --- |
| 1. Power outages that affected water system facilities during the 30 days prior to the TC+ or EC + findings | Y N |  |  |
| 2. Water line flushing or fire fighting event | Y N |  |  |
| 3. Inadequate disinfection during and after repairs or new construction (example: pipe repair, well repair, new tank) | Y N |  |  |
| 4. Any other issues/problems/sources of contamination that may have caused the positive coliform result (e.g. vandalism; unauthorized access…) | Y N |  |  |

SUMMARY:  Based on the results of the investigation and any other available information, what is believed to be the cause(s) of the E. coli positive or multiple total coliform positive sample(s) from the public water system?

CORRECTIVE ACTIONS:  What actions has the water system taken to correct the above mentioned issue(s)? If additional time is needed to correct a deficiency, indicate the date that it will be corrected.

COMPLETED BY (NAME): 	     	REG. AGENCY:		     		DATE: 	MM/DD/YYYY

Additional comments: